## Sheet1
Automatic Fire Suppression Coverage Areas
Mini | Volume | Height | Width | Depth |  | Quartzoid Bulb Detector (QBD) Value
100g | 0.130Mᶾ | 260 | 1000 | 500 |  | Colour | Ambient Temp | Bulb Rating
200g | 0.261Mᶾ | 1000 | 520 | 500 |  | Orange | 40ᵒC | 57ᵒC | UK Stock
300g | 0.392Mᶾ | 1000 | 780 | 500 |  | Red | 50ᵒC | 68ᵒC | Special Order
400g | 0.520Mᶾ | 1250 | 300 | 500 |  | Yellow | 60ᵒC | 79ᵒC
500g | 0.780Mᶾ | 1300 | 300 | 500 |  | Green | 80ᵒC | 93ᵒC | Special Order
[6 empty] | Blue | 127ᵒC | 141ᵒC
Launcher | Distance | Volume | (Wall mounted @1.5m) |  |  | Purple | 168ᵒC | 182ᵒC
4Kg | 2.5m | 9Mᶾ |  |  |  | Black | 242ᵒC | 260ᵒC
6Kg | 3.0m | 12Mᶾ
9Kg | 3.5m | 20Mᶾ |  |  |  | CQRS
[6 empty] | Agent | KG | Mᶾ
CM ABC | Max Height | Diameter | Areas exceeding these values for protection to use multiple AtomX units |  |  | Fk-5-1-12 | 1 | 1
5Kg | 3.2m | 4M² |  |  |  | CO² | 1.85 | 1
10Kg | 4.0m | 6M²
CM FK-5-1-12 | 21ᵒC | Max Mᶾ | Areas exceeding these values for protection to use multiple AtomX units |  |  | CM | Ceiling Mounted System
5kG | V/wt 7% | 10Mᶾ
10kG | V/wt 7% | 20Mᶾ
Wall mounted Inverted Extinguisher 68ᵒC QBD
MAP90 | Coverage | FK-5-1-12 | Coverage | Size | Coverage
1Kg | 1.0M² | 1Kg | 1.4Mᶾ | 6Kg | 8.5Mᶾ
2Kg | 2.5M² | 1.5Kg | 2.1Mᶾ | 9Kg | 12.8Mᶾ
4Kg | 2.0M² | 2Kg | 2.8Mᶾ
6Kg | 2.5M² | 2.5Kg | 3.5Mᶾ
9Kg | 4.0M² | 4Kg | 5.7Mᶾ
FK-5-1-12 |  | Sustainably Engineered
Feature |  |  |  | Benefit
Low pressure (17Bar) |  |  |  | Lower Container and valve cost, Safer to Handle
Zero ODP <1 GWP |  |  |  | Environmentally Friendly
Cools and chemically interferes with the Chemical Reaction |  |  |  | More efficient fire fighting agent
Denser / Heavier than Air |  |  |  | Less quantity required per volume
Can be transported via Airfreight as a liquid |  |  |  | Cheaper to transport
No Risk to Life |  |  |  | Much higher safety margin
Do not require F Gas to handle |  |  |  | Available to all users